## Заявка - request
Приложение: №1. Форма коммерческого предложения / Attachment: №1. Commercial proposal form
Полное наименование юридического лица / Company name:
Телефон / Telephone:
Адрес электронной почты / E-mail address:
Ф.И.О. контактного лица / Contact person
№ | Наименование Товара / Name of Goods | Описание Товара | Description of the Goods | Ед. изм. / Unit | Кол-во / Quantity | Цена за 1 единицу / Unit Price USD/Долларов США | Стоимость / Total Price Value USD/Долларов США | Страна происхождения/Изготовитель/ Country of Origin/ Manufacturer
1 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 6x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF CI 6x2x1,5 Цвет серый. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 6x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI 6x2x1,5 Color: grey. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.6
2 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 4x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF CI 4x2x1,5. Цвет серый. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 4x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 =100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI 4x2x1,5. Color: grey. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. CI-fire resistant. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 =100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
3 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 2x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF CI Цвет серый. 2x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 2x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс:1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI Color: grey. 2x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 2x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
4 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 12x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF CI. Цвет красный. 12x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х-Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 12x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов всистемах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI. Color: red. 12x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х-XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 12x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов всистемах контроля и управления. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
5 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 4x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF CI. Цвет красный. 4x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 4x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс:1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI. Color: red. 4x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.8
6 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 6х2х1,5 | Кабель RE-2X(St)HSWAH+PIMF CI. Цвет голубой. 6x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 6x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс:1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI. Color: light blue. 6x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.7
7 | Кабель (Cable) RE-2X(St)HSWAH+PIMF CI 4х2х1,5 | Кабель RE-2X(St)HSWAH+PIMF CI. Цвет голубой. 4x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 4x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс:1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI. Color: light blue. 4x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
8 | Кабель (Cable) RE-2X(St)HSWAH+PIMFCI 2х2х1,5 | Кабель RE-2X(St)HSWAH+PIMF CI. Цвет голубой. 2x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. CI-огнестойкий. Число и сечение жил: 2x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000 В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс:1,50 мм2 = 100 пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF CI. Color: light blue. 2x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 2x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
9 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 20x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет серый. 20x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. Число и сечение жил: 20x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2 000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 20x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 20x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2 000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 1
10 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 10x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет серый. 10x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. Число и сечение жил: 10x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2 000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 10x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 10x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2 000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
11 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 8x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет серый. 8x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. Число и сечение жил: 8x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 8x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 8x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
12 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 6x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет серый. 6x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. Число и сечение жил: 6x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 6x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
13 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 4x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет серый. 4x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. Число и сечение жил: 4x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 4x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
14 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 2x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет серый. 2x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF-Индивидуальный экран пары. Число и сечение жил: 2x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 2x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 2x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
15 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 20x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 20x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 20x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минима льный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 20x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 20x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. minима льный радиус изгиба: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.8
16 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 18x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 18x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 18x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 18x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 18x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.7
17 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 16x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 16x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 16x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение : 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 16x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 16x2x1,5. Rated voltage U0/U:300/500 V. Test voltage : 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 1
18 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 12x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 12x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 12x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 12x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 12x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 1
19 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 10x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 10x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 10x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 10x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 10x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 1
20 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 8x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 8x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 8x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 8x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 8x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.5
21 | Кабель (Cable) RE-2X(St)HSWAH+PIMF 6x2x1,5 | Кабель RE-2X(St)HSWAH+PIMF. Цвет голубой. 6x2x1,5. RE- Скрученный проводник из мягкой отожженной электролитической меди. 2Х- Изоляция из сшитого полиэтилена (XLPE). (St) -Общий экран. Н- Внутренняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. SWA- Броня из стальной проволоки. H- Внешняя оболочка из малодымного, безгалогенного трудновоспламеняющегося компаунда LSZH. PIMF -Индивидуальный экран пары. Число и сечение жил: 6x2x1,5. Номинальное напряжение U0/U:300/500 B. Тестовое напряжение: 2000В. Сопротивление проводника: 1,50 мм2 = 12,1 Ом/км. Сопротивление изоляции, мин.: 5000 МОм х км. Рабочая ёмкость, макс: 1,50 мм2 = 100пФ/м. Температурный диапазон: от -30°С до +90°С. Отношение индуктивности к сопротивлению L/R: 1,50 мм2 = 40 мгн/Ом. Минимальный радиус изгиба: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов в системах контроля и управления. Востребован на электростанциях, в химической и нефтедобывающей промышленности. Допускается внутренняя и наружная прокладка, в сухих и влажных помещениях. | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 6x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.65
Условия оплаты / Payment terms:
Срок поставки / Delivery time:
Условия поставки / Delivery terms (Incoterms):

## English
№ | Name of Goods | Description of the Goods | Unit | Quantity | Unit Price USD | Total Price Value USD | Country of Origin / Manufacturer
1 | Cable RE-2X(St)HSWAH+PIMFCI 6x2x1,5 | Cable RE-2X(St)HSWAH+PIMF CI 6x2x1,5 Color: grey. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.6
2 | Cable RE-2X(St)HSWAH+PIMFCI 4x2x1,5 | Cable RE-2X(St)HSWAH+PIMF CI 4x2x1,5. Color: grey. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. CI-fire resistant. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 =100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
3 | Cable RE-2X(St)HSWAH+PIMFCI 2x2x1,5 | Cable RE-2X(St)HSWAH+PIMF CI Color: grey. 2x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 2x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
4 | Cable RE-2X(St)HSWAH+PIMFCI 12x2x1,5 | Cable RE-2X(St)HSWAH+PIMF CI. Color: red. 12x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х-XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 12x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 В. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Предназначен для передачи цифровых и аналоговых сигналов всистемах контроля и управления. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
5 | Cable RE-2X(St)HSWAH+PIMFCI 4x2x1,5 | Cable RE-2X(St)HSWAH+PIMF CI. Color: red. 4x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.8
6 | Cable RE-2X(St)HSWAH+PIMFCI 6х2х1,5 | Cable RE-2X(St)HSWAH+PIMF CI. Color: light blue. 6x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.7
7 | Cable RE-2X(St)HSWAH+PIMF CI 4х2х1,5 | Cable RE-2X(St)HSWAH+PIMF CI. Color: light blue. 4x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
8 | Cable RE-2X(St)HSWAH+PIMFCI 2х2х1,5 | Cable RE-2X(St)HSWAH+PIMF CI. Color: light blue. 2x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. CI-fire resistant. Number and size: 2x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000 V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max:1,50 mm2 = 100 pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
9 | Cable RE-2X(St)HSWAH+PIMF 20x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 20x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 20x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2 000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 1
10 | Cable RE-2X(St)HSWAH+PIMF 10x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 10x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 10x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2 000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
11 | Cable RE-2X(St)HSWAH+PIMF 8x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 8x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 8x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
12 | Cable RE-2X(St)HSWAH+PIMF 6x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 6x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
13 | Cable RE-2X(St)HSWAH+PIMF 4x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 4x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 4x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
14 | Cable RE-2X(St)HSWAH+PIMF 2x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: grey. 2x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF-Individual pair screen. Number and size: 2x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
15 | Cable RE-2X(St)HSWAH+PIMF 20x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 20x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 20x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. minима льный радиус изгиба: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.8
16 | Cable RE-2X(St)HSWAH+PIMF 18x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 18x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 18x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.7
17 | Cable RE-2X(St)HSWAH+PIMF 16x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 16x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 16x2x1,5. Rated voltage U0/U:300/500 V. Test voltage : 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 1
18 | Cable RE-2X(St)HSWAH+PIMF 12x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 12x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 12x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 1
19 | Cable RE-2X(St)HSWAH+PIMF 10x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 10x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 10x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 1
20 | Cable RE-2X(St)HSWAH+PIMF 8x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 8x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 8x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | KM | 0.5
21 | Cable RE-2X(St)HSWAH+PIMF 6x2x1,5 | Cable RE-2X(St)HSWAH+PIMF. Color: light blue. 6x2x1,5. RE- Stranded conductor made of soft annealed electrolytic copper. 2Х- XLPE Insulation. (St) -Static screen. Н- Inner shell of low smoke, halogen-free flame retardant compound LSZH. SWA- Steel wire armor. H- Outer shell made of low smoke, halogen-free flame retardant compound LSZH. PIMF -Individual pair screen. Number and size: 6x2x1,5. Rated voltage U0/U:300/500 V. Test voltage: 2000V. Conductor resistance: 1,50 mm2 = 12,1 Ohm / km. Insulation resistance, min.: 5000 Megohm x km. Working capacity, max: 1,50 mm2 = 100pF/m. Temperature range: from -30°С to +90°С. The ratio of inductance to resistance L/R: 1,50 mm2 = 40 Mg / Ohm. Minimum bending radius: 10 x ?. Designed for transmitting digital and analog signals in control and management systems. It is in demand at power plants, in the chemical and oil industry. Allowed indoor and outdoor installation, in dry and wet rooms. | КМ | 0.65